## Calculator
Medical Gas Consumption Calculator v4.12.20
Created by Prof. Robert L. Chatburn, MHHS, RRT-NPS, FAARC 2020
| Goal | Estimate medical gas consumption by mechanical ventilators
| Note | Some ventilators have blowers and do not consume air from the wall outlet
| Abbreviations | BTPS = body temperature and pressure saturated with water vapor
|  | STPD = standard temperature and pressure dry |  |  | correction factor
Minute Ventilation (STPD) = Minute Ventilation (BTPS) x conversion factor:
DOV = duration of ventilation per patient
L = Dm3
BASIC ASSUMPTIONS | units | High | Median | Low
Barometric Pressure | mmHg | 760
Atmospheric Temperature | °C | 27
Minute Ventilation | L/min/vent; BTPS | 12 | 7.84 | 5
Minute Ventilation | L/min/vent; STPD | 9.9142 | 6.4773 | 4.1309
FiO2 |  | 1 | 0.6 | 0.4
Oxygen Flow | L/min/vent; STPD | 9.9142 | 3.1976 | 0.99351
Oxygen Flow | L/hr/vent; STPD | 594.8526 | 191.8588 | 59.6108
Oxygen Flow | L/d/vent; STPD | 14276.4632 | 4604.6112 | 1430.6582
Air Flow | L/min/vent; STPD | 0 | 3.2796 | 3.1374
Air Flow | L/hr/vent; STPD | 0 | 196.7783 | 188.2445
Air Flow | L/d/vent; STPD | 0 | 4722.6781 | 4517.8681
CRITICAL ASSUMPTIONS | units | High | Median | Low
Daily Ventilator Census | vents | 800 | 500 | 100
Duration of Ventilation | days | 14 | 12 | 10
Total vent-days | vent-days | 11200 | 6000 | 1000
Capacity of Oxygen H-Tanks | L/tank | 7080
Capacity of Air H-Tanks | L/tank | 7080
RESULTS for PIPING SYSTEMS (STPD) | units | High | Median | Low
Oxygen Consumption Rate/min | cubic Dm or L | 7931.3684 | 1598.8233 | 99.3513
Oxygen Consumption Rate/hr | cubic Dm or L | 475882.1053 | 95929.3991 | 5961.0759
Oxygen Consumption Rate/day | cubic Dm or L | 11421170.5263 | 2302305.5776 | 143065.8228
Air Consumption Rate/min | cubic Dm or L | 0 | 1639.8188 | 313.7408
Air Consumption Rate/hour | cubic Dm or L | 0 | 98389.1272 | 18824.4504
Air Consumption Rate/day | cubic Dm or L | 0 | 2361339.054 | 451786.8088
1 |  | 1
RESULTS for TANK SYSTEMS (STPD) | units | High | Median | Low
Required Oxygen H-Tanks per Day | tanks | 1613.1597 | 325.1844 | 20.207
Required Oxygen H-Tanks per Population Duration of Ventilation | tanks | 22584.2355 | 3902.2128 | 202.0704
Required Air H-Tanks per Day | tanks | 0 | 333.5225 | 63.8117
Required Air H-Tanks per Population Duration of Ventilation | tanks | 0 | 4002.2696 | 638.117
References
https://www.amazon.com/Handbook-Respiratory-Robert-Chatburn-2010-07-23/dp/B01K3QB92S/ref=sr_1_4?dchild=1&keywords=chatbun+handbook&qid=1586113909&sr=8-4-spell
https://www.mdpi.com/2071-1050/10/8/2948
https://www.beaconmedaes.com/en/guru/publications
https://urldefense.com/v3/__https:/www.dropbox.com/s/nbh6sitchxzbg36/KP*20White*20Paper*20Medical*20Air*20and*20Oxygen*20Capacity*20v3.pdf?dl=0__;JSUlJSUlJSU!!BZ50a36bapWJ!8y-bJUh7uaVnwynU3u42kCeEFuOEdW2SWg8XvBk22wnmnsQU4oynH4_-dQdivjRt88w$
cubic decimeters (L)
cubic feet

## Data - reference
Reference | https://www.amazon.com/Handbook-Respiratory-Robert-Chatburn-2010-07-23/dp/B01K3QB92S/ref=sr_1_4?dchild=1&keywords=chatbun+handbook&qid=1586113909&sr=8-4-spell
Sumary COVID-19 Patient Data